## S01
|  |  | WORK ORDER | S01
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Gravity Main
TASK DESCRIPTION | Annual Sanitary Main Inspection |  | RECEIVED BY:
FREQUENCY | Annual (est. 7.9 labor hours/km of sanitary main)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual inspection of sanitary main, manhole and sewer flow
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Traffic Cones, Safety Harness, Spotlight, Mirrors, Power Rodder
MATERIALS REQUIRED | Yellow Epoxy Paint, Cement/Grout
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Review all equipment before leaving workshop
Barricade off all work area when in traffic areas.
Note conditions of manhole structure especially infiltration at joints and around frame, repair with waterproofing cement grout.
Prepare list of observed maintenance and repair work required.
Inspect interior of sewer pipe. If there is evidence of siltation or the accumulation of solids, use rodding equipment to remove or engage qualified contractor. Additionally note any areas which are in need of possible repairs.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Illumination
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff
Confined Spaces
Traffic Control

## S02
|  |  | WORK ORDER | S02
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Gravity Main
TASK DESCRIPTION | Main Flushing and Cleaning |  | RECEIVED BY:
FREQUENCY | Every 3 Years (est. 11.4 labor hours/km of sanitary main)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Flushing of sanitary main every 5 years
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Jet Cleaning Ball, Poly Rope, Manhole Jack, Hand Pump, Fire Hose, Hydrant Wrench, Manhole lifter, 2.5" Valve
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
This task is to be coordinated with watermain hydrant flushing task.
Start at the head of each sewer run and proceed to work downstream.
Open manhole cover and downstream manhole cover and ventilate as required.
Connect hose to fire hydrant valve and backflow preventer. Hold the nozzel firmly at the top of the manhole. Never place the fire hose directly into the manhole.
Have the same person operate all the hydrants as the cleaning progresses. It is very important to have a separate person with clean clothing handling the hydrants to avoid contamination of the water system.
Starting from the upstream sanitary manhole, flush each sanitary main until water runs clear in downstream manhole.
Pack up equipment, turn off hydrants, and proceed to the next manhole to flush the next pipe section. Repeat until all sewers and manholes have been cleaned.
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Traffic Control

## S03
|  |  | WORK ORDER | S03
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Gravity and Force Mains
TASK DESCRIPTION | CCTV Inspection |  | RECEIVED BY:
FREQUENCY | Every 10 Years (est. 2.2 labor hours/km of sanitary main)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | CCTV Inspection of Sanitary Distribution and Collection Mains
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Traffic Cones
MATERIALS REQUIRED | N/A
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Retain certified CCTV inspection company to perform inspection of system.
Supervise inspection, update maintenance log noting any required repairs.
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
Traffic Control

## S04
|  |  | WORK ORDER | S04
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Gravity and Force Mains
TASK DESCRIPTION | Vac Truck |  | RECEIVED BY:
FREQUENCY | As Required
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Vac Truck
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Traffic Cones
MATERIALS REQUIRED | N/A
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Retain certified Vac Truck company for service as required.
N/A
 Inform Homeowners  Inform Agencies  Inform Staff

## S05
|  |  | WORK ORDER | S05
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Force Mains
TASK DESCRIPTION | Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 1.25 labor hrs/km of forcemain)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual Force Main Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Shovel
MATERIALS REQUIRED | N/A
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S05
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Walk along all forcemain right-of-ways and check for signs of dampness, or accumulation of water which may indicate leakage. Check notable trench settlement, indicating material washout and potential leak. If potential leak is suspected, dig out immediate area by shovel, sufficient to confirm leak present.
Note: Forcemain cleanout chamber is a confined space - do not enter.
Open cover to forcemain cleanout chamber and vent as required.
From ground level, note any leakage from valve or joints.
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Confined Spaces

## S06
|  |  | WORK ORDER | S06
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Backflow Preventor
TASK DESCRIPTION | Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 1 labour hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Backflow Preventor/Double Check Valve inspection by certified inspection and service crew
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED | N/A
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S06
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Confined Spaces
Contract certified service technicians shall carry out a complete inspection and servie of backflow preventer and double check valve.
Observe tasks performed by qualified service technicians, and make notes.

## S07
|  |  | WORK ORDER | S07
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Wastewater Air Release Valve
TASK DESCRIPTION | Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Bi-Annual (est. 0.5 labour hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Inspection and maintenance of Air Release Valves at sanitary system high points
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED | N/A
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | S07
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Confined Spaces
Carry out an inspection to verify operation of each Air Release Valve.
Check unit and pipe connections for any leakage.
With the inlet shut-off valve open, partially open the drain valve until flow can be heard. If the Air Release Valve is working properly, water should be exhausted from the drain valve. If a large amount of air is exhausted, valve requires backwash procedure and/or service.
Contract certigied service technicians to trouble-shoot the cause and rectify.

## LS01
|  |  | WORK ORDER | LS01
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Lift Station
TASK DESCRIPTION | Weekly Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Visual and auditory inspection of lift station
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED | Generator Fuel
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | LS01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually/audibly inspect the lift station. Check for signs of damage/vandalism.
Record pump hours for each pump. Check for uneven pump run times.
Wash down the wet well.
Check for sand and sludge accumulation.
Check for indication of high water levels.
Inspect lights and alarm systems.
Ensure adequate fuel levels in the generator and ensure no fluid leaks.
Complete inspection form
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment

## LS02
|  |  | WORK ORDER | LS02
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Lift Station
TASK DESCRIPTION | Monthly Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 1.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Visual and auditory inspection of lift station
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log, Control Panel Keys
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | LS02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually inspect each pump for proper pumping (run each pump by manual control, watch level rise and fall.)
Pump down wet well to lowest point, and make visual inspection.
Check wet well floats.
Exercise suction and discharge valves.
Test back-up generator - check engine coolant and oil level and battery charger. SEE WORK ORDER GEN01
Complete inspection form.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
Additional Work Orders: GEN01
 Inform Homeowners  Inform Agencies  Inform Staff

## LS03
|  |  | WORK ORDER | LS03
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Lift Station
TASK DESCRIPTION | Quarterly Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Quarterly (Every Three Months) - est. 3 labor hrs
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Visual and auditory inspection of lift station
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log, Control Panel Keys
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | LS03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Remove excessive grit & grease with VAC truck (if required).
Test generators, under load, for 15 minutes.
Inspect pumps (visually check pumps and piping for defects, record amperage readings for each pump).
Clean and inspect floats.
Complete inspection form.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## LS04
|  |  | WORK ORDER | LS04
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Lift Station
TASK DESCRIPTION | Semi-Annual Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Semi Annual (est. 6 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Thorough inspection and cleaning of lift station
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log, Control Panel Keys
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | LS04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Work to be completed by O&M staff or by a certified Lift Station Servicing Contractor
Record pump hours.
Conduct Generator Maintenance GEN02
Complete inspection form.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
Additional Work Orders: GEN02
 Inform Homeowners  Inform Agencies  Inform Staff

## LS05
|  |  | WORK ORDER | LS05
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Lift Station
TASK DESCRIPTION | Annual Inspection and Maintenance
FREQUENCY | Annual (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Thorough inspection and cleaning of lift station
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log, Control Panel Keys
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | LS05
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Work to be completed by O&M staff or by a certified Lift Station Servicing Contractor
Record pump hours.
Open panel, megger all pumps.
Run all pumps and check their current.
Visually inspect control panel.
Visually inspect pump tank, tank hatches, guide rails and guid rail holders.
Check functionality of check valves.
Visually inspect flush valve, check flush valve oil if necessary, change oil or totally rebuilding flush valve on site if needed.
Re-arrange pump cable and chain if needed for easy removal of pumps.
Pull pumps and ressure wash while still in tank to minimize surface contamination.
Visually inspect pumps, lifting handle, chain, cable, colute face, and the stator and oil chamber plugs for wear.
Replace lifting handle, chain, stator and oil chamber plugs on site if needed.
Check the stator and oil chamber for oil level and water infiltration.
Inspect impeller.
Test run pumps out of tank to listen for noisy bearings, vibrations or abnormal operation and rotation.
Inspect existing zincs or install new ones depending on pump condition.
Lower pumps back into tank.
Test run pumps and check their current. Ensure pumps are pumping down the effluent in the station. Ensure pumps are seated properly.
Inspect float switches, clean off if necessary.
Make sure float switch levels are correct.
Run through float switch cycle if needed.
Replace float switch on site if needed.
Ensure all breakers are on and pump switches are set to auto before leaving.
Ensure all alarms are reset.
Complete inspection form.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## LS06
|  |  | WORK ORDER | LS06
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Collection |  | START DATE | END DATE
ASSET COMPONENT | Lift Station
TASK DESCRIPTION | Pump out and Flush Wet Well - Vac Truck |  | RECEIVED BY:
FREQUENCY | Annual (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Pump out and Flush Wet Well - Vac Truck
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses, gloves
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | LS06
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Make arrangements to have a qualified vac truck contractor pump out and flush wet well.
N/A
 Inform Homeowners  Inform Agencies  Inform Staff

## GEN01
|  |  | WORK ORDER | GEN01
ASSET |  |  | ORDER DATE
ASSET GROUP | OTHER |  | PO#
ASSET SUBGROUP | Electrical |  | START DATE | END DATE
ASSET COMPONENT | Backup Generator
TASK DESCRIPTION | Monthly Generator Maintenance |  | RECEIVED BY:
FREQUENCY | Monthly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly Generator Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log, multimeter
MATERIALS REQUIRED | Coolant and oil as required
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  | 1 |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | GEN01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Inspect enclosure.
Check engine coolant level.
Check engine oil level.
Replace fuel as required.
Check the battery charger.
Complete inspection form.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## GEN02
|  |  | WORK ORDER | GEN02
ASSET |  |  | ORDER DATE
ASSET GROUP | OTHER |  | PO#
ASSET SUBGROUP | Electrical |  | START DATE | END DATE
ASSET COMPONENT | Backup Generator
TASK DESCRIPTION | Generator Servicing |  | RECEIVED BY:
FREQUENCY | Annual
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Generator servicing with certified technician
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log, Control Panel Keys
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | GEN02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Retain a certified generator maintenance technician to preform annual servicing.
N/A
 Inform Homeowners  Inform Agencies  Inform Staff

## W01
|  |  | WORK ORDER | W01
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Monthly Distribution System Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 0.3 hr/km of watermain)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly inspection of distribution system
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Valve wrench set, Valve pick
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Walk or drive along all watermain rights-of-way and check for signs of dampness, or accumulation of water or ice, which may indicate leakage.
Check that all hydrants and standpipes are straight up and down. Clear any vegetation around them to make them easily visible/accessible.
Check that all valve box lids, hydrant caps, and other appurtenances are in place. Set back in place if missing, repair damage.
Locate and expose all valve boxes. Open alll valve box lids to ensure they are accessible. Check all main valves and ensure valve stem is vertical. Movement of valves could indicate failure due to fracture or misalignment.
Close and open main valves and check for leaks. After operating each valve ensure that it is left in its normal operating position.
Record locations of any new main valves and services on as-built drawings and O&M manual
Survey the residents to check for leaks, lack of pressure, dirty water, and water taste (chlorine)
Note any signs of excessive water usage.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W02
|  |  | WORK ORDER | W02
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Valve Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 3.3 labour hrs/km of watermain)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Locate, inspect, and perform maintenance on valves
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, valve key
MATERIALS REQUIRED | Lubricants and epoxy paint as required
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Notify Administration Office, Campground Office, and Fire Department that water supply will be interrupted. Review all equipment before leaving the yard.
Remove valve box top and clean out debris etc. from box, if applicable. Remove sand, etc. from valve and lubricate gears, bolts, etc.
Work valve (opening an closing) slowly until confident that valve is closed when shut. All valves close by turning valve stem clockwise. Check for leaks. Check if valve is vertical, movement of valves could indicate possible failure due to fracture or misalignment.
Proceed to next valve and repeat above steps to isolate the section of watermain.
Check with consumers connected to isolated section to determine if valve is functioning properly (i.e. water is shut off). If water is still available, repeat Steps 3 to 6 until valve is functioning properly. If still unable to operate valve correctly after 3 attempts, contact Engineer and band office.
Before leaving a valve fully open, turn clockwise one half turn to prevent the valve from sticking.
Proceed to next section (Paint valve boxes with epoxy yellow and mark with stake if required)
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Fire Department  Inform Staff

## W03
|  |  | WORK ORDER | W03
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Watermain Flushing |  | RECEIVED BY:
FREQUENCY | Annual (est. 8 labor hr/km of watermain)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual Watermain Flushing
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Hydrant wrench / hydrant pump, fire hose
MATERIALS REQUIRED | Lubricants and epoxy paint as required
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Mains are flushed by opening hydrants creating high flows in mains to flush out silt, rust, etc.
Notify all affected water users that system is being flushed.
Ensure reservoir is full.
Start at hydrant closest to where supply main joins distribution system. Attach fire hose and run hose to ditch or sewer manhole to control water. (If hose run into sewer, coordinate with sewer flushing task S02.)
Open hydrant fully and flush for 10 minutes or until water runs clear.
Slowly close hydrant, grease threads lightly, and replace port caps.
Pick up hoses, move to next hydrant downstream, and repeat until all mains are flushed.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W04
|  |  | WORK ORDER | W04
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Hydrant Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 4.7 labor hrs/km of watermain)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual inspection and maintenance of fire hydrants
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Hydrant wrench / hydrant pump, valve key
MATERIALS REQUIRED | Lubricants and epoxy paint as required
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Notify Administration Office, Campground Office, and Fire Department that water supply will be interrupted.
With outlet nozzel cap closed, open the hydrant fully until the stem stops turning.
If stem action is tight, open and close it a few times until operation is smooth and free.
If there is leakage at the joints, packing seals, or nozzels, close hydrant and lubricate, tighten or replace packing, nozzles gaskets, and O rings. (Use jet-lube on operating nut and AP-5 on nozzles. These are lubricants non-destructive to rubber lined fire hose).
With the hydrant closed, remove a nozzle cap.
Look and listen for water that continues to flow indicating leakage through the main valve, if there is a leak, make a note and arrange for repairs.
Open the hydrant and flush out debris for 1 minute. (If a hose is used to redirect the water, then after flushing, close the hydrant, removed hose and re-open hydrant until water flows from nozzle).
Remove independent cut-off nozzle cap, where present, fully open and close valve to ensure ease of operation. Lubricate if required and check that there is an unrestricted flow of water through the nozzle.
Close the hydrant and check for drainage by putting hand over nozzle and feeling for suction, replace cap only when suction stops. If there is no suction or if water is observed in the barrel, open the hydrant until water discharges from the nozzle. This action should flush the hydrant drain. Shut the hydrant and recheck for suction. Hydrants with blocked or permanently plugged drains should be marked and pumped out after each usage.
Clean and lubricate nozzle threads.
If any leakages cannot be corrected with tools at hand or if hydrant is inoperable, close auxiliary valve. Inform Fire Department and promptly arrange to have repairs carried out.
Check that hydrant is reassembled properly and functional. Paint the hydrants if required.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Fire Department  Inform Staff

## W05
|  |  | WORK ORDER | W05
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | PRV
TASK DESCRIPTION | PRV Inspection (Contractor) |  | RECEIVED BY:
FREQUENCY | Annual
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual check of Water Meters and PRV
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Meter Box Key
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W05
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Make arrangements to have a qualified contractor inspect PRV.
N/A
 Inform Homeowners  Inform Agencies  Inform Staff

## W06
|  |  | WORK ORDER | W06
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | PRV
TASK DESCRIPTION | PRV Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Weekly check of Water Meters and PRV
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Meter Box Key
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W06
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check for leaks from valves and fittings.
Check all valves are turned to open position.
Check operation of PRVs. Compare pressure gauge reading upstream and downstream of pressure reducing valve. Confirm downstream gauge set to system operating pressure.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W07
|  |  | WORK ORDER | W07
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Mains
TASK DESCRIPTION | Winterizing Water System |  | RECEIVED BY:
FREQUENCY | Twice annually (drain November, reactivate March) |  | (est. 0.5 labor hr/hydrant)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Drain hydrants to winterize water system
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Hydrant wrench / hydrant pump, valve key
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W07
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Drain hydrants to prevent freezing. Open hydrant to allow flow out port.
Close hydrant valve.
Turn hydrant nut to closed position.
Replace port cap.
Contact fire department to inform them of works done.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Fire Department  Inform Staff

## W08
|  |  | WORK ORDER | W08
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Watermain
TASK DESCRIPTION | Watermain Spot Repairs |  | RECEIVED BY:
FREQUENCY | As needed (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Watermain Spot Repairs
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, backhoe, compactor, mud pump, hand tools
MATERIALS REQUIRED | Sand bedding, gravel, repair sleeves, couplings, pipe
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W08
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Ensure that the equipment is operative before leaving yard.
Obtain BC 1 Call ticket to confirm locations of underground services (oil, propane, power, sewer, watermains and services). Check available plans.
Proceed to designated area and set out required safety devices and signs.
If there is no flooding of homes, etc., leave main line on and:
a. have consumers notified
- to store any required water during the interruption
- probable duration of water service interruption
b. then locate the break in main line pipe by any means necessary (leak detector, drilling holes in pavement, checking for noise on meters and/or curb boxes)
c. shut off valves required to isolate main
If there is flooding of homes etc., the main line must be shut off immediately. Then proceed through previous steps to notify consumers and isolate break in the main.
Notify Administration Office and fire department of number and location of hydrants involved.
Notify Administration Office and fire department of required traffic rerouting (streets closing and detours).
Excavate.
Repair pipe at damaged spot using required repair clamps.
Check elevations for local depressions and repair pipe bedding where necessary.
Open main line valves. Check new section of pipe and joints for leakage.
If leakage is observed, shut off valves to isolate main line and carry out corrective action. Repeat previous step to ensure leakage is resolved.
Slowly open hydrants only to remove air, rust, and sand from watermain.
Backfill around the pipe and 300mm over the pipe with clean granular material less than 25mm in size. Compact by hand in 150mm lifts to give firm support for the pipe. Ensure that no large rocks come in contact with pipe or repair clamps.
Backfill excavation above the pipe zone with native soil in 200mm layers. Compact each layer with compactor.
Notify Administration Office and fire department that the watermain and hydrants are back in service.
Repair travelled surface as needed, remove equipment and clean up area.
Have health unit monitor the chlorine residual and notify the Administration Office when the water has been disinfected.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Traffic Control
 Inform Homeowners  Inform Fire Department  Inform Staff

## W09
|  |  | WORK ORDER | W09
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Curb box/stop
TASK DESCRIPTION | Curb Box and Curb Stop Repairs |  | RECEIVED BY:
FREQUENCY | As needed (est. 6 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Curb Box and Curb Stop Repairs
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, backhoe, compressor and blowpipe, tamper, hand tools
MATERIALS REQUIRED | Varies with repair
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W09
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check equipment before leaving yard to ensure it is in working condition.
Proceed to designated area and set out required safety devices and signs.
Blow out curb box with compressor. Note: If curb box requires repair proceed as follows:
Obtain location of utilities from telephone, gas, and hydro companies if required.
Remove sod as required, and excavate and expose curb box foot and curb stop.
Check condition and carry out necessary repairs.
Backfill excavation with native soil, compact with tamper in 300mm lifts to grade.
Repair surface to original, remove equipment, and clean up area.
As required: locate, mark, and paint each house connection to curb stop valve box.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W10
|  |  | WORK ORDER | W10
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Fire Hydrant and Standpipe
TASK DESCRIPTION | Fire Hydrant and Standpipe Test |  | RECEIVED BY:
FREQUENCY | 3 times per year (every 3 months except in winter) |  | (est. 2 labor hrs/hydrant)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Fire Hydrant and Standpipe Test
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Hydrant wrench / hydrant pump, valve key
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W10
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Test the operation and condition of each hydrant.
Locate and open the valve to the main. Adjust the valve box to a level slightly above the adjacent ground or 150mm below grade in travelled roadway. Paint the valve box with yellow epoxy.
Check the standpipes for water tightness, listen to the valve key for the sound of running water indicating underground leakage. If leakage is detected or suspected, schedule standpipe for repair.
Check hydrant for completeness of cap. Replace if necessary.
Attach fire hose to hydrant (standpipe) and run to nearest ditch.
Locate open 150L drum adjacent to ditch.
Slowly open hydrant valve directing fire hose into ditch. Ensure air gap is maintained between nozzle and any part of manhole to prevent contamination of nozzle. On completion treat nozzle liberally with bleach to disinfect.
Direct hose discharge into empty 150L barrel, and record in seconds the time required to fill the barrel.
A. 150L in _________sec = __________L/s
B. 150L in _________sec = __________L/s
C. 150L in _________sec = __________L/s
Note size of fire hose and nozzle hose diameter
Hose diameter ____________mm
Nozzle diameter____________mm
Distance from standpipe to nozzle ___________m
Direct fire flow stream to its maximum horizontal distance to an area that is level with the operator. Measure the maximum distance travelled by the fire stream.
Horizontal drop _____________m
A. Maximum distance __________m
B. Maximum distance __________m
C. Maximum distance __________m
Allow fire stream into the ditch for a five minute period, taking care to prevent contamination of the nozzle.
Close hydrant slowly. Wait five minutes for hydrant body to drain before replacing cap. Test to ensure hydrant has drained. If hydrant does not drain, note for repair.
Empty test barrel, replace manhole cover, and grease.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W11
|  |  | WORK ORDER | W11
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Valve
TASK DESCRIPTION | Valve Repair |  | RECEIVED BY:
FREQUENCY | As required (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Valve Repair
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, valve key, backhoe, compactor, mud pump, misc. hand tools
MATERIALS REQUIRED | Valves, repair clamps, sand bedding
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W11
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check equipment before leaving yard.
Obtain location of sewer and water lines and connections.
Notify Administration Office and fire department of water service interruption.
Excavate and remove extra fill, expose valve, and check condition.
Shut off appropriate valves.
Remove bonnet, spindle, and gates. Check condition.
Cut out obsolete valve if it cannot be repaired on site. Install new valve of required size with MOA pipe and repair clamps.
Re-open main valves and check for leaks. If leakage exists, shut off valves and make repairs as necessary. Repeat to confirm leakage is resolved.
Blow out designated hydrants and pump out.
Place 450mm of granular material as bedding for the valve. Backfill excavation with native soil 200mm layers and compact each layer with tamper.
Repair surface as necessary and clean up area.
Notify Administration Office, consumers, and fire department that work is complete.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Fire Department  Inform Staff

## W12
|  |  | WORK ORDER | W12
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Hydrant
TASK DESCRIPTION | Hydrant Repair (General) |  | RECEIVED BY:
FREQUENCY | As required (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Hydrant Repair (General)
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, backhoe, compactor, mud pump, hand tools
MATERIALS REQUIRED | Varies by repair
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W12
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check equipment before leaving yard.
Notify Administration Office, consumers, and fire department of water service interruption.
Shut off necessary main valves.
Excavate to expose hydrant lead and carry out necessary repairs.
Open main valves and check for leakage. If leakage is observed, close main valves and carry out required repairs. Repeat until no leakage is observed.
Backfill excavation with native soil in 200mm layers and compact each layer with a compactor. Repair surface and clean up area.
Notify Administration Office and fire department of work completion.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Fire Department  Inform Staff

## W13
|  |  | WORK ORDER | W13
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Hydrant
TASK DESCRIPTION | Hydrant Repairs (Internal) |  | RECEIVED BY:
FREQUENCY | As required (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Hydrant Repairs (Internal)
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, hydrant wrench, hand tools
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W13
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check equipment before leaving yard.
Contact Administration Office and notify fire department of number and location of hydrants not in service.
Shut off hydrant auxiliary valve, remove bonnet.
Open hydrant auxiliary valve and pump out hydrant to test proper functioning.
If hydrant operates correctly, proceed to next designated hydrant. If not, repeat steps until it is working correctly.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Fire Department  Inform Staff

## W14
|  |  | WORK ORDER | W14
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Hydrant
TASK DESCRIPTION | Hydrant Painting |  | RECEIVED BY:
FREQUENCY | Every 3 years (est. 0.5 labour hr/hydrant)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Hydrant Painting
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, paint brushes, rags, number stencils
MATERIALS REQUIRED | Paint
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W14
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Paint fire hydrants fire red.
After paint has dried (next day), paint yellow identification numbers on hydrants.
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W15
|  |  | WORK ORDER | W15
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Air Release Valve Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Semi-Annual (est. 1 labor hr/valve)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Semi-annual inspection of air release valves
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W15
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Carry out an inspection to verify operation of each Air Release Valve
Check unit and pipe connections for any leakage.
With the inlet shut-off valve open, partially open the drain valve until flow can be heard. If the air release valve is working properly, water should be exhausted from the drain valve. If a large amount of air is exhausted, valve requires backwash procedure and/or service.
Contract certified service technicians to trouble-shoot the cause and rectify.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
Confined Space
 Inform Homeowners  Inform Agencies  Inform Staff

## W16
|  |  | WORK ORDER | W16
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Chlorine Residual Test |  | RECEIVED BY:
FREQUENCY | Monthly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Chlorine Residual Test
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE (gloves and safety glasses), Maintenance Truck, chlorine residual test kit
MATERIALS REQUIRED | Chlorine test chemicals
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W16
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Choose four residential test locations
Turn on a cold water faucet and let the water run about one minute or until fresh.
Take a water sample, following the instructions supplied with the test kit.
File correspondence and, if necessary, take medial measures such as increasing or decreasing chlorine dosing concentrations. Typically, residual chlorine readings should not be less than 0.1 mg/L at any location within the distribution system.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W17
|  |  | WORK ORDER | W17
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Water Quality Check |  | RECEIVED BY:
FREQUENCY | Monthly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Water Quality Check
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck
MATERIALS REQUIRED | Sample bottles provided by Health Canada
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W17
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Turn on a cold water faucet and let the water run about one minute or until fresh.
Take a water sample, following the instructions supplied with the sample bottle.
Ship the sample container in a cooler box to Health Department as soon as possible after sampling.
File correspondence and, if necessary, take medial measures such as increasing chlorine dosing concentrations, cleaning reservoir, or flushing pipes.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W18
|  |  | WORK ORDER | W18
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Watering Points Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Monthly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Watering Points Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, wrenches
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W18
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check all watering points to make sure taps and lines are not leaking or frozen. Repair or remove ice as required.
Report any major problems to Administration Office (frozen or broken water lines)
Check caps
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## W19
|  |  | WORK ORDER | W19
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply / Distribution |  | START DATE | END DATE
ASSET COMPONENT | Main
TASK DESCRIPTION | Air Release Valve Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 2 labor hrs/valve)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual inspection of air release valves
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | W19
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Contract certified service technicians shall carry out a complete inspection and service of each Air Release Valve
Air Release Valve Chamber is a confined space - do not enter without appropriate training, procedures, and equipment.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
Confined Space
 Inform Homeowners  Inform Agencies  Inform Staff

## WT01
|  |  | WORK ORDER | WT01
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Chlorine Disinfection Treatment System
TASK DESCRIPTION | Daily Inspection |  | RECEIVED BY:
FREQUENCY | Daily (est. 0.5 labor hrs/station)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Daily inspection of Chlorine Disinfection Treatment System (check all stations)
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually/audibly inspect the treatment plan and surrounding area. Check for signs of damage/vandalism.
Check solution level in the tank: refill if necessary and be sure to replace the cover. (Ensure chlorine mixing procedure is posted in treatment building.)
Visibly mark solution tank
Check for excessive chlorine odor or visible leaks. Repair leaks if required. Ensure adequate ventilation.
Check pump for unusual warmth or vibration that could indicate damaged bearings or gears.
Test free chorine residual in distribution system using an EPA approved test kit.
Evaluate and log results - note consistency of free chlorine levels in log book.
Adjust pump feed-rate control as required.
Record results of all tests, chemical use, water production, and maintenance in daily logbook.
Check records of logbooks for unusual data, trends and other indicators or possible problems.
Keep copy of chlorination treatment system O&M manual in treatment building.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WT02
|  |  | WORK ORDER | WT02
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Chlorine Disinfection Treatment System
TASK DESCRIPTION | Quarterly Inspection |  | RECEIVED BY:
FREQUENCY | Quarterly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Quarterly inspection and Maintenance of Chlorine Disinfection Treatment System
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Calibration tools, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Calibrate chemical feed pump to verify the performance of the pump output - follow manufacturer's instructions
Wash and clean the chlorine solution tank if there is any sediment build-up. Clean the chlorinator, lines and foot valve as needed - follow manufacturer's instructions.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Manufacturer's Instructions
 Inform Homeowners  Inform Agencies  Inform Staff

## WT03
|  |  | WORK ORDER | WT03
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Chlorine Disinfection Treatment System
TASK DESCRIPTION | Annual Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 4 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual inspection and Maintenance of Chlorinator
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, back-up chemical feed pump, Inspection Log
MATERIALS REQUIRED | Spare Parts Kit (o-rings, valves)
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Clean the chlorinator and replace the O-rings, valves, and worn or damaged parts - use the spare parts kit to make repairs and follow manufacturer's instructions. You should have a back-up chemical feed pump to provide continuous disinfection.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
Manufacturer's Instructions
 Inform Homeowners  Inform Agencies  Inform Staff

## WT04
|  |  | WORK ORDER | WT04
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Water Treatment Plant
TASK DESCRIPTION | Daily Inspection |  | RECEIVED BY:
FREQUENCY | Daily (7 days/week) (est. 0.5 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Daily Inspection (7 Days per Week)
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Record turbidity, colour, and chlorine residual
Adjust chlorine feed rate if necessary
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WT05
|  |  | WORK ORDER | WT05
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Water Treatment Plant
TASK DESCRIPTION | Week Day Inspection |  | RECEIVED BY:
FREQUENCY | Weekdays (5 days/week) (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Water Treatment Plant Week Day Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT05
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Record raw water flowmeter reading
Record 24 hour production for filters from flowmeter
Record filter flow rates
Record treated water flow
Record raw and filtered water turbidity
Record raw and filtered water colour
Record raw water temperature
Record chlorine usage and residual
Adjust chlorine feed rate if necessary
Record piezometer levels for filter headloss
Adjust filter production rate in PLC if necessary
Inspect water treatment facility
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WT06
|  |  | WORK ORDER | WT06
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Water Treatment Plant
TASK DESCRIPTION | Periodic Inspection and Test |  | RECEIVED BY:
FREQUENCY | Weekly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Water Treatment Plant Periodic Inspection and Test
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT06
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Conduct periodic jar tests to optimize alum dosage and adjust alum feed pump accordingly
Once per week measure pH, alkalinity, and hardness of trated water
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WT07
|  |  | WORK ORDER | WT07
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Water Treatment Plant
TASK DESCRIPTION | Filter Scraping |  | RECEIVED BY:
FREQUENCY | 6 times/year (est. 16 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Filter Scraping
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, shovels, wheelbarrow
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT07
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
NOTE: All equipment should be clean and shovels, boots, and wheelbarrows should be dedicated solely for this task to avoid possible contamination of the filters.
Shut off inflow to filter to be scraped
Decant unfiltered water to just above sand surface by opening filter draw down valve to drain
Lower water to 30cm below filter sand surface using underdrain valve
Lay 25mm x 250mm planks across filter sand for working surface; do not walk on unscraped filter sand
Remove top 1 to 2cm of sand using square headed shovel and wheelbarrow and discard
Rake sand level
Slowly refill filter by backfeeding from bottom through underdrain with filtered water from active filter to just above sand
Fill filter part way up with unfiltered water input through draw down line
Fill and run filter using raw water inlet line
Waste filtered water until good quality water is being produced
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WT08
|  |  | WORK ORDER | WT08
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Water Treatment Plant
TASK DESCRIPTION | Media Addition |  | RECEIVED BY:
FREQUENCY | Every 6 years (est. 60 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Water Treatment Plant Media Addition
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, bobcat
MATERIALS REQUIRED | Sand
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WT08
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Follow WT07 for scraping filter
After scraping filter, further drain underdrain piping by opening filter drain valve to waste (if necessary for inspection of underdrains etc.)
Resand filter and spread evenly
Follow procedure in WT07 for refilling filter after scraping
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WW01
|  |  | WORK ORDER | WW01
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Groundwater Well
TASK DESCRIPTION | Weekly Maintenance |  | RECEIVED BY:
FREQUENCY | Weekly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Weekly or daily groundwater well inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Enclosure Keys, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WW01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check well house interior (if applicable) and grounds for general cleanliness and condition, and for any threats to water quality
Check any warning lights or alarms - low water level in the well, intrusion, power outage, pump failure, and so on.
Read source water meter. Record water-production data in well house log.
Check pump-cycling rate. If it runs continuously or cycles more than 6 times per hour, see pump troubleshooting.
Check well house building or fenced enclosure for signs of security problems - graffiti, vandalism, doors or locks damaged etc.
Check wells source site after any adverse weather - high winds, heavy snow, ice, rains, etc.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WW02
|  |  | WORK ORDER | WW02
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Groundwater Well
TASK DESCRIPTION | Monthly Maintenance |  | RECEIVED BY:
FREQUENCY | Monthly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly groundwater well inspection and maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WW02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check well water level if source capacity is marginal or there are drought conditions.
Check area for excessive vegetation or dangerous conditions - uncut grass, brush, dead trees, fire hazard, etc.
Check well house control valves for proper positions, open or closed. Post information.
Check source control system - pressure switch settings, cycling, pressure tanks, storage tank water levels, etc.
Check well house control valves for damage or leaks.
Check for leaks - read source meter when you expect the water usage to be zero.
Check source pump cycling and pressure switch settings, on/off pressures and line pressures.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WW03
|  |  | WORK ORDER | WW03
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Groundwater Well
TASK DESCRIPTION | Annual Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 3 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual groundwater well inspection and maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Tools for exercising valves, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WW03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check well site for water ponding, poor drainage areas, excessive vegetation, unhealthy trees, fire hazards, etc.
Check source facilities conditions - corrosion, vent screens, vehicular or other damage, animal activity, etc.
Check cold weather protection - insulation, heating system, alarm system etc.
Verify sanitary integrity of the sources - screened vents, no unprotected openings, electrical box sealed.
Evaluate source using designations (permanent, seasonal, emergency, inactive)
Exercise valves and test run emergency source wells to waste. Do not supply distribution system without WQ tests.
Evaluate Emergency Response Plan and update as required.
Review source related customer complaints and evaluate corrective actions and planning.
Implement seasonal start-up or shut-down procedures as required.
Review source water quality test results for trends, such as increasing nitrate or seasonal coliform problems.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WW04
|  |  | WORK ORDER | WW04
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Groundwater Well
TASK DESCRIPTION | Periodic Maintenance |  | RECEIVED BY:
FREQUENCY | Every 3 years (est. 4 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Periodic well assessment
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WW04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Measure source pump capacity in gallons per minute (GPM) to detect pump output problems.
Evaluate general source capacity to meet water system demand. Use water use and production records.
Evaluate capacity of source water to provide water of a reliable quantity and quality acceptable to customers.
Consider television inspection of the well interior and the well screens
If the source capacity is marginal or drought conditions are present, develop and implement a Conservation Plan.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## BS01
|  |  | WORK ORDER | BS01
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Boost Station
TASK DESCRIPTION | Weekly Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Weekly or daily boost station inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, temperature gage, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | BS01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check pump house interior and grounds for general cleanliness and condition.
Check any warning lights or alarms for low pressure, pump failure, intrusion, power outage.
Check pumps for leaks or seepage for pumps that are not water lubricated.
Check motor for unusual pump motor conditions such as:
Unusual pump noises in operation (hum, chattering, clicking, rapid knocking)
Motor fails to start or to come up to speed normally
Blackened or excessive sparking at communtator or brushes
Fine dust under couplings with rubber butters or pins
Smoke or charred insulation
Excessive vibration
Check pump cycle rate - troubleshoot excessive pump cycling (about 6 cycles per hour)
Verify start and stop pressure settings and operability of water pressure gauges - reference O&M manual.
Check bearing temperatures - if a temperature gauge is available. Take care when checking how hot it may be.
Check and record pump run hours.
Check condition of the pump house and booster pump stations for damage and deterioration.
Check area around the pump house and booster station for security concerns, vandalism or unauthorized access.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## BS02
|  |  | WORK ORDER | BS02
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Boost Station
TASK DESCRIPTION | Monthly Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Monthly (est. 4 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly Booster station inspection and maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | BS02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check oil or grease lubricant reservoirs for proper levels and any leakage or unusual conditions.
Measure the pump capacity, compare with the expected output - from performace records or design parameter.
Perform routine operation of emergency generator per manufacturer's instructions - check condition of emergency gneerator batteries, fuel levels, oil levels, instruments and controls. SEE GEN01
Check that the existing pressure gauges pump run meters and flow meters are functioning properly.
Check that pump controls are functioning properly
Check pump house lighting, ventilation, heating, and animal proofing (birds, bats, rodents)
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
Additional Work Orders: GEN01
 Inform Homeowners  Inform Agencies  Inform Staff

## BS03
|  |  | WORK ORDER | BS03
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Distribution |  | START DATE | END DATE
ASSET COMPONENT | Boost Station
TASK DESCRIPTION | Annual Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 6 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual Boost Station Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, O&M Manual, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | BS03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Evaluate the working condition of all pumps and schedule maintenance, overhaul, or replace.
Review emergency response plans and update as needed.
Review O&M manual and update as necessary
Review the adequacy, reliability and redundancy of the current pumping facilities and plan for improvements.
Review financial capacity to complete expected maintenance or replacement to existing pumping facilities.
Measure source pump capacity in gallons per minute (GPM) to detect pump output problems.
Evaluate the design of existing pump facilities and plan for improvements.
Verify pressure gagues are available to monitor pump capacity.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WS01
|  |  | WORK ORDER | WS01
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Water Storage
TASK DESCRIPTION | Weekly Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Daily or Weekly Inspection of Water Storage Facility
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WS01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check any warning lights or alarms - low water level, hight water level, intrusion, power outage, and so on.
Check storage tank for signs of security breaches - damaged fences, open gates, graffiti, vandalism, etc.
Check water level indicator - functioning, adequate amount of stored water, excessive water use.
Check the overflow line, vents, ladder access locks, roof access hatches, and controls that are readily visible from the ground for damage, vandalism, or other conditions.
Check storage tank and site after any adverse weather - high winds, heavy snow, ice, rains, etc.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WS02
|  |  | WORK ORDER | WS02
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Water Storage
TASK DESCRIPTION | Monthly Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 3 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly Inspection and maintenance of Water Storage Facility
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WS02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check water level indicator
Verify all openings are protected from surface runoff, windblown contaminants, insects, birds and animals.
Check tank overflow lines for signs of damage, such as, screens, flapper valves, check valves, splash plate, etc.
Check area for excessive vegetation or dangerous conditions - uncut grass, brush, dead trees, fire hazard, etc.
Check control valves for proper positions, open or closed
Check control valves for damage or leaks.
Check low water temperature alarm - cold weather only.
Check high water temperature limit switch - when heating system in service.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WS03
|  |  | WORK ORDER | WS03
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Water Storage
TASK DESCRIPTION | Quarterly Inspection |  | RECEIVED BY:
FREQUENCY | Quarterly (est. 3 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Quarterly Inspection and maintenance of Water Storage Facility
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WS03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check water level indicator
Visually inspect tank exterior and roof for signs of damage, corrosion, degradation, leakage or structural problems, with particular focus on all openings into the reservoir (reservoir roof and sidewall vents access hatch, overflow outlet, and so on.)
Check tank-supporting structure for signs of damage, corrosion, degradation, structural inadequacy.
Tank catwalks/ladders free from signs of damage, corrosion, degradation, structural condition, vandalism, etc.
Tank area for water ponding, poor drainage areas, excessive vegetation, unhealthy trees, fire hazards, etc.
Tank area free from combustible storage, trash, debris, brush, or other material that could present a fire hazard.
Tank area free of accumulation of material on or near parts possibly resulting in accelerated corrosion or rot.
Tank and support free of ice buildup.
Check earth embankments for erosion, burrowing animals, improper drainage and leakage.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WS04
|  |  | WORK ORDER | WS04
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Water Storage
TASK DESCRIPTION | Annual Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 4 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual Inspection and maintenance of Water Storage Facility
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Tools for exercising valves, Inventory, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WS04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check storage tank structural, seismic and sanitary integrity - leaks, corrosion, cracks, supports, warping, etc.
Inspect storage tank interior for pitting, concrete spalling, rot, corrosion, rust, water level sensors, biofilm build-up etc.
Exercise valves and make repairs as needed.
Inventory and evaluate storage facilities capacity, condition, replacement costs and plan for improvements.
Evaluate stored water for clarity, sediments, floating materials or films, unusual odors, insects birds or animals.
Plan for storage facility improvements and budget for the associated costs.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## WS05
|  |  | WORK ORDER | WS05
ASSET |  |  | ORDER DATE
ASSET GROUP | WATER |  | PO#
ASSET SUBGROUP | Supply |  | START DATE | END DATE
ASSET COMPONENT | Water Storage
TASK DESCRIPTION | Three Year Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Every 3 Years (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Three to Five Year Inspection and Maintenance of Water Storage Facility
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Maintenance Truck, Inspection Log
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | WS05
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Tank indicator inspected - every three years for steel storage tanks without corrosion protection
Tank indicator inspected - every five years for storage tanks other than steel without corrosion protection
Drain, inspect, clean, and disinfect storage tank or use a diving maintenance service without draining tank.
Respond to any evidence of storage tank problems.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST01
|  |  | WORK ORDER | ST01
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Bi-Annual Lagoon Inspection |  | RECEIVED BY:
FREQUENCY | Bi-Annual (est. 3 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Bi-Annual Lagoon Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety Glasses, wrench set
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST01
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually inspect effluent pump, alarms and controls to ensure they are in adequate operating condition as per SMP section 3.7.7.5
Test alarm operation including a physical test with a float
Check all plumbing fittings and ensure piping is in operating condition
Measure and record water level in lagoon below berm top
Visually inspect fencing
Maintain vegetation as required.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST02
|  |  | WORK ORDER | ST02
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon Facility
TASK DESCRIPTION | Monthly Lagoon Facility Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 1.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly Lagoon Facility Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety Glasses, wrench set
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST02
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Ensure vegetation shall be maintained at a height not more than 6" above the ground on lagoon dykes
Not more than 10% of the water surface shall be covered by floating vegetation and not more than 10% of the water perimeter may have emergent rooted aquatic plants.
Inspect for dike damage caused by erosion or animal burrowing and correct immediately
Inspect integrity of the lagoon liner, correct immediately if deficiencies noted.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST03
|  |  | WORK ORDER | ST03
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Septic Tank / Field (Type 1)
TASK DESCRIPTION | Septic Tank Pumping |  | RECEIVED BY:
FREQUENCY | As Required (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Septic Tank Pumping
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety Glasses, wrench set
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST03
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Retain certified septic tank pumping company to pump tanks as required.
Ensure that tanks pumped during winter conditions are refilled immediately and that all plastic tanks are refilled immediately.
Pumping out of the tank should be shceduled at the most fabourable time of the year in terms of freezing temperatures and groundwater.
Some digestion of sludge and reduction of sludge volume occurs after approximately 3 years, it is therefore not appropirate to pump out tanks when pumping is not required.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST04
|  |  | WORK ORDER | ST04
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Septic Tank / Field (Type 1)
TASK DESCRIPTION | Monthly Septic Tank and Field Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Quarterly Septic Tank and Field Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety Glasses, wrench set
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST04
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually inspect for sludge and scum accumulations. Inspect for clogging, damage, and proper placement of outlet baffle and filter. Clean filter and replace if damaged or deteriorating.
Record signs of leaking or infiltration in tanks, penetrations, and risers. Repair or replace as necessary.
Look for signs of overflow/seepage probelms
Ensure risers and lids are above grade with secure lids, and surface water is directed away from lids.
Ensure floats are functioning properly. Check that float actuates alarm when moved to "on" position. Clean and repair as necessary.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST05
|  |  | WORK ORDER | ST05
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Septic Tank / Field (Type 1)
TASK DESCRIPTION | Bi-Annual Septic Tank and Field Inspection |  | RECEIVED BY:
FREQUENCY | Bi-Annual (est. 3 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Bi-Annual Septic Tank and Field Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety Glasses, wrench set
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST05
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually inspect for sludge and scum accumulations. Pump when sludge and scum thickness total 1/3 of the depth of the tank or as directed in the maintenance plan.
Inspect for clogging, damage, and proper placement of outlet baffle and filter. Clean filter and replace if damaged or deteriorating.
Record signs of leaking or infiltration in tanks, penetrations, and risers. Repair or replace as necessary.
Look for signs of overflow/seepage probelms
Ensure risers and lids are above grade with secure lids, and surface water is directed away from lids.
Ensure floats are functioning properly. Check that float actuates alarm when moved to "on" position. Clean and repair as necessary.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST06
|  |  | WORK ORDER | ST06
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Effluent pump station, RBC Module, secondary clarifiers, chlorination equipment, dechlorinator
TASK DESCRIPTION | Sewage Treatment Plant Inspection |  | RECEIVED BY:
FREQUENCY | Daily (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Sewage Treatment Plant Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED | Chlorine tablets, sodium thiosulphate
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST06
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check that all components are secure and that there is no sign of vandalism.
Check that all switches on the control panel are in their proper operating position.
Check that all components are operating.
Check for signs of leakage.
Check chlorinator. Add chlorine tablets when required. Ensure that tablets lie flat.
Check sodium thiosulphate level. Replenish when required.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST07
|  |  | WORK ORDER | ST07
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Effluent pumps, chamber
TASK DESCRIPTION | Effluent Pump Station Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Weekly (est. 0.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Effluent Pump Station Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST07
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Inspect system to ensure that pumps are cycling properly in automatic mode.
Record pump hours for each pump.
Ensure that the float switches are hanging freely and are clear of debris.
Simulate pump operations by raising floats to ensure proper operation.
Remove any obstacles which may cause blockage of pumps.
NOTE: Pumps should be serviced annually by a qualified Contractor.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST08
|  |  | WORK ORDER | ST08
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Effluent pump chamber, overflow return line
TASK DESCRIPTION | Effluent Pump Station Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Effluent Pump Station Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, hose
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST08
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Carry out weekly inspection (ST08).
Flush out overflow return line.
Hose down interior of chamber.
NOTE: Shut down RBC drive if flushing from RBC bucket chamber.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST09
|  |  | WORK ORDER | ST09
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | RBC Unit
TASK DESCRIPTION | RBC Module Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | RBC Module Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, grease gun, misc. hand tools
MATERIALS REQUIRED | Lubricant, oil
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST09
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check to ensure that sludge is not accumulating in the RBC chamber.
If sludge has accumulated, schedule pump out at time of septic tank pump out.
Do not wash down RBC discs.
Check chain drive oil bath, replenish as required.
Every three (3) months the roller bearing must be greased. Refer to manufacturer's brochures for information.
NOTE: any major servicing required should be carried out by a qualified Contractor. Shut down RBC drive prior to carrying out any servicing.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
Manufacturer's Instructions
 Inform Homeowners  Inform Agencies  Inform Staff

## ST10
|  |  | WORK ORDER | ST10
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Secondary clarifiers, sludge return pumps, pipe
TASK DESCRIPTION | Secondary Clarifiers Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Daily (est. 0.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Secondary Clarifiers Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, squeegee
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST10
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Monitor sludge accumulation and adjust frequency of sludge return pump operation as necessary.
Gently brush any sludge from walls of chamber to bottom.
Skim and dispose of any scum floating on surface or accumulated against baffle.
Check air vacuum valve for free operation and flush with clean water as required.
NOTE: No adjustment of pumps during inspection and maintenance is required. Once per year thet pumps should be serviced by a qualified Contractor.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST11
|  |  | WORK ORDER | ST11
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Chlorinators, chlorine contact tank
TASK DESCRIPTION | Chlorinators and Tank Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Chlorinators and Tank Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, chlorine test kit
MATERIALS REQUIRED | Chlorine tablets
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST11
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Carry out daily tasks.
Monitor chlorine residual at outlet from contact chamber and adjust number of tubes in use as appropriate.
Check that nothing is floating in the tank.
Check quantity of chlorine tablets and reorder as required.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST12
|  |  | WORK ORDER | ST12
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Chlorinators, chlorine contact tank
TASK DESCRIPTION | Chlorinators and Tank Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Annual (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Chlorinators and Tank Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED | Chlorine
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST12
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Drain chlorine contact tank.
Rinse baffles and walls and flush out any solids which have settled.
Inspect baffles for any sign of damage.
Refill tank.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST13
|  |  | WORK ORDER | ST13
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Dechlorination vat and pump
TASK DESCRIPTION | Dechlorinator Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Weekly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Dechlorinator Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, chlorine test kit
MATERIALS REQUIRED | Sodium thiosulphate
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST13
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Carry out daily tasks.
Check pump to ensure that pump operates when flow passes through works.
Test effluent to ensure that chlorine residual is neutralized and adjust dechlorination pump as necessary.
Check quantity of sodium thiosulphate and reorder as required.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST14
|  |  | WORK ORDER | ST14
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Flow Recorder
TASK DESCRIPTION | Flow Recorder Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 0.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Flow Recorder Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED | Flow recording strip
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST14
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Replace flow recording strip as required (once every 30 days)
Check recorder float to ensure free operation of mechanism.
Replace pen as required.
Record date and total flow.
Calibrate flow recorder if required. As per Wastewater Systems Effluent Regulations, monitoring equipment must be calibrated at least once in every calendar year.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
Wastewater Systems Effluent Regulations [https://www.gazette.gc.ca/rp-pr/p2/2012/2012-07-18/html/sor-dors139-eng.html]
 Inform Homeowners  Inform Agencies  Inform Staff

## ST15
|  |  | WORK ORDER | ST15
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Outfall pipe
TASK DESCRIPTION | Outfall Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Outfall Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST15
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check and make sure that sewage is not backing up due to a blockage in the line.
During low tides check that the pipe has not been damaged.
Collect sample of effluent and send for testing as required by Wastewater Systems Effluent Regulations.
Any required maintenance should be carried out by a qualified Contractor.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Wastewater Systems Effluent Regulations [https://www.gazette.gc.ca/rp-pr/p2/2012/2012-07-18/html/sor-dors139-eng.html]
 Inform Homeowners  Inform Agencies  Inform Staff

## ST16
|  |  | WORK ORDER | ST16
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Flume Chamber
TASK DESCRIPTION | Flume Chamber & Sewage Flow Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Bi-Weekly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Flume Chamber & Sewage Flow Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST16
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Flume Chamber is a confined space - do not enter
Open cover and ventilate, as required
Note condition of structure including benching and channel
Check parshall flume insert for blockages and misalgnment.
Note any material build-up in channel causing restriction to flow. Clean as required
Check cutrasonic level unit for grease build-up. Wipe off grease with rag, as required
Replace chamber cover.
Yearly - hose down chamber, benching, channel and fittings.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Wastewater Systems Effluent Regulations [https://www.gazette.gc.ca/rp-pr/p2/2012/2012-07-18/html/sor-dors139-eng.html]
 Inform Homeowners  Inform Agencies  Inform Staff

## ST17
|  |  | WORK ORDER | ST17
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Sanitary Treatment - Influent Screen
TASK DESCRIPTION | Monthly Influent Screen Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly inspection of influent screen
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety Glasses, wrench set
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST17
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Inspect screen for wear and tear.
Inspect fasteners.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST18
|  |  | WORK ORDER | ST18
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Sanitary Treatment- Spray Pump
TASK DESCRIPTION | Monthly Spray Pump Inspection |  | RECEIVED BY:
FREQUENCY | Monthly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly inspection of spray pump
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST18
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check packing on pump and adjust to 5 drops per minute.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST19
|  |  | WORK ORDER | ST19
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Sanitary Treatment - Dosing Pump
TASK DESCRIPTION | Chemical Dosing Pump Maintenance |  | RECEIVED BY:
FREQUENCY | Quarterly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Quarter annual cleaning of chemical dosing pump foot valve and injection tube
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses, gloves
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST19
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Work to be completed only by Trained and Qualified Personnel
Isolate dosing pump and flush pump.
Clean foot valve and valve boxes.
Clean injection tube.
Return pump to service.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST20
|  |  | WORK ORDER | ST20
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Flocculator Tank
TASK DESCRIPTION | Semi-annual Flocculator Tank maintenance |  | RECEIVED BY:
FREQUENCY | Semi Annual (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Semi annual inspection and cleaing of flocculator tank
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses
MATERIALS REQUIRED | Tank touch up paint
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST20
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Work to be completed only by Trained and Qualified Personnel
Isolate tank.
Drain and clean tank.
Inspect tank and tank coating.
If coating is marked up, touch up paint is required.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST21
|  |  | WORK ORDER | ST21
`
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Sanitary Treatment - Filter
TASK DESCRIPTION | Semi-annual filter maintenance |  | RECEIVED BY:
FREQUENCY | Semi Annual (est. 1.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Semi annual inspection and cleaing of lift station filter
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses, gloves
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST21
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Work to be completed only by Trained and Qualified Personnel
Check valve seals for leakage. Replace as needed.
Check pressure guage condition. Replace as needed.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST22
|  |  | WORK ORDER | ST22
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Sanitary Treatment - Dosing Pump
TASK DESCRIPTION | Semi-annual Chemical Dosing Pump Maintenance |  | RECEIVED BY:
FREQUENCY | Semi Annual (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Semi annual inspection and cleaing of chemical dosing pump
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses, gloves
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST22
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Work to be completed only by Trained and Qualified Personnel
Check pump output at varying pump speeds (100%, 75%, 50%, and 25%).
Verify that the pump output volume is consistant with manufactures specifications.
Worksafe/Occupational Health & Safety Regulations:
Working Alone or in Isolation
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST23
|  |  | WORK ORDER | ST23
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Annual Rock Filter Inspection |  | RECEIVED BY:
FREQUENCY | Annual (est. 8 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Annual Rock Filter Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, Safety glasses, gloves, air compressor and air hose
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST23
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Hire air compressor and air hose to suit bubbler type algae cleaning system.
Attach air hose line to 1/4" quick connect fitting in Effluent Pumphouse.
Open check valves fully in air line chamber, to allow air to feeder lines in rock filter.
Start compressor to pump air to rock filter and dislodge any algae build up.
Observe downstream chamber for extent of algae removal. Check effluent for clarity and odours.
Inspection/Pumpout Chamber - inspect for algae build up in spring and fall. Pump out as required.
Flush/rod cleanouts as required to remove algae build up.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST24
|  |  | WORK ORDER | ST24
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Mechanical Aerators Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Week Days (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Week Day Mechanical Aerator Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST24
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Observe all aerators are in operation and that proper aeration action is present in lagoon cells. Note steady circular water motion throughout all areas of cells (observe foam, etc. on surface)
Visually check from shore all floats and mountings, swing arm assembly, mooring cables, and anchor posts.
A 'snoring' noise indicates air entrapment. Rectify by adjusting shaft to steeper angle during quarterly maintenance task.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST25
|  |  | WORK ORDER | ST25
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Mechanical Aerators Inspection and Maintenance |  | RECEIVED BY:
FREQUENCY | Quarterly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Quarterly Mechanical Aerator Inspection and Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, maintenance truck, boat/paddles, life jackets, adjustable wrench
MATERIALS REQUIRED | Grease
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST25
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Note: 2 persons required for safety.
Grease aerators every 3 months as recommended by manufacturer.
A 'snoring' noise indicates air entrapment. Rectify by adjusting shaft to steeper angle.
Check all bolts, fittings, and attachments are secure. Tighten as required. Note any mooring cable stretch.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST26
|  |  | WORK ORDER | ST26
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Weir and Bypass Chambers Inspection |  | RECEIVED BY:
FREQUENCY | Weekly (est. 0.25 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Weekly Weir and Bypass Chambers Inspection
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST26
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Visually inspect all weir and bypass chamber structures, including gates and seals. Note operating levels are normal. Particular attention should be given to the first bypass chamber in the lagoon system which collects the most solids build up, grease, debris, etc.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST27
|  |  | WORK ORDER | ST27
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Weir and Bypass Chambers Inspection & Maintenance |  | RECEIVED BY:
FREQUENCY | Monthly (est. 0.5 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Monthly Weir and Bypass Chambers Inspection & Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, fire hose
MATERIALS REQUIRED
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST27
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Hose down bypass chambers and remove solids built up, grease, floatables, debris, etc.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST28
|  |  | WORK ORDER | ST28
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Weir and Bypass Chambers Inspection & Maintenance |  | RECEIVED BY:
FREQUENCY | Quarterly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Quarterly Weir and Bypass Chambers Inspection & Maintenance
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, fire hose
MATERIALS REQUIRED | Grease
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST28
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
Check fibreglass access grating for stability and note any signs of cracking, delaminating, loose fittings, etc. Operate all weir and bypass gates by opening and closing all the way to prevent mechanism from seizing. Grease stems as required. Outlet flows resulting from this exercise will be directed either to next cell in lagoon system, or to effluent wet well.
Hose down chambers and gates to remove grease and solids build up, as required.
Worksafe/Occupational Health & Safety Regulations:
Personal Protective Clothing and Equipment
 Inform Homeowners  Inform Agencies  Inform Staff

## ST29
|  |  | WORK ORDER | ST29
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Effluent Quality Check |  | RECEIVED BY:
FREQUENCY | Monthly (est. 2 labor hrs)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Effluent Quality Check at Sewage Lagoon
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE, sampling rod
MATERIALS REQUIRED | Sample bottles
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST29
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Wastewater Systems Effluent Regulations [https://www.gazette.gc.ca/rp-pr/p2/2012/2012-07-18/html/sor-dors139-eng.html]
Fill out label on sample bottle as per laboratory requirements
Indicate location and testing for Bacterial Oxygen Demand (BOD) and Total Suspended Solids (TSS)
Attach sample bottle to end of sampling rod. Feed sample through opening in grating and immerse in effluent entering lagoon. Collect sample.
Repeat at other chambers, collecting samples both upstream and downstream of rock filter as applicable.
Wash hands, rinse off sampling rod and sample bottles. Place bottles in a cooler box with an ice pack. It is important to keep the samples cool or refrigerated prior to shipping.
Ship the cooler box with sample bottles for independent testing of sewage effluent quality (BOD and TSS) within 4 hours of sampling.
Upon sample results return, check compliance with regulatory parameters and action as required.

## ST30
|  |  | WORK ORDER | ST30
ASSET |  |  | ORDER DATE
ASSET GROUP | SANITARY |  | PO#
ASSET SUBGROUP | Treatment |  | START DATE | END DATE
ASSET COMPONENT | Lagoon
TASK DESCRIPTION | Effluent Leakage Check |  | RECEIVED BY:
FREQUENCY | Semiannual (est. 1 labor hr)
KEY CONTACTS
ASSET DESCRIPTION
WORK LOCATION
WORK DESCRIPTION | Effluent Leakage Check at Sewage Lagoon
TYPICAL OPERATING CONDITION
COMMUNICATIONS REQUIRED
EQUIPMENT REQUIRED | PPE
MATERIALS REQUIRED | Sample bottles
LABOR DESCRIPTION |  | HOURS | RATE | AMOUNT
Maintenance Supervisor |  |  |  | 0
Maintenance Assistant |  |  |  | 0
Truck |  |  |  | 0
Contractor |  |  |  | 0
Equipment |  |  |  | 0
Parts + Materials |  |  |  | 0
LABOR TOTAL |  |  |  | 0
REFERENCE DOCUMENTS
|  |  | WORK ORDER | ST30
WORK DESCRIPTION
COMPLETION NOTES
q Updated Maintenance Logs and Inspection Forms
COMPLETED PROJECT VALUE | $ | HOURS TO COMPLETE
REASON FOR VARIANCE
PARTS USED
 Inform Homeowners  Inform Agencies  Inform Staff
Worksafe/Occupational Health & Safety Regulations:
Ergonomics (MSI) Requirements
Personal Protective Clothing and Equipment
Wastewater Systems Effluent Regulations [https://www.gazette.gc.ca/rp-pr/p2/2012/2012-07-18/html/sor-dors139-eng.html]
Fill out label on sample bottle as per laboratory requirements
Indicate location and testing for fecal coliform only.
Collect sample at underdrain discharge outlet.
Wash hands and rinse off sample bottle. Place bottle in a cooler box with an ice pack. It is important to keep the sample cool or refrigerated prior to shipping.
Ship the cooler box with sample bottles for independent testing within 4 hours of sampling.
Upon sample results return, check for indication of fecal bacteria, which may indicate leakage in lagoon liner membrane.